## README
CaptiveAire / Evergreen Telemetry field worksheets – cleaned reference copy
Source: tb-worksheet-evergreen 2.xlsx (kept as backup). Job data removed; formulas unchanged except:
- Supply Fan Filters: VLOOKUP now uses exact match (FALSE).
- PSP Supply: CFM/ft returns blank instead of #DIV/0! when the block is empty; blanks count treated as 0.
Constants used by the a2b TAB workbook ({Dropdowns} sheet, columns H:Z):
Exhaust baffle filters (VelGrid): CFM = velocity x free area x K, K = 1.34 Captrate / 1.28 baffle (rev 2.1)
Supply fan filters (VelGrid): CFM = velocity x free area x 1.35 (rev 1)
Condensate baffle / HVC slot (Airfoil): CFM = average of 3 readings x probe constant (rev 0)
PSP supply (VelGrid): CFM = avg of readings x (length - 2 - 2 x blanks) x width x K / 144, K = 0.88 (<=12 in) or 0.95 (>=14 in) (rev 2)
Direct-fired burner profile pressure: CFM by housing size 1-5, linear interpolation between table points (rev 1)
Note: the exhaust and supply tables list slightly different free areas for the same nominal filter size
(e.g. 16x20: 1.73 vs 1.75 sq ft). Both are carried as published; confirm the current values with CaptiveAire.

## Exhaust with Baffle Filters
Exhaust Baffle Filter CFM Worksheet for Evergreen VelGrid
Job Number = | [11 empty] | rev. 2.1
Job Name =
Hood Number 1 Information | [13 empty] | Filter Information |  |  |  |  | Filter Reference Data | [11 empty] | Filter Type Selection | Flter Type Data
Model = |  | Length = |  |  | Notes: | [8 empty] | Reference | Filter Size | Free Area | Captrate K Factor | Baffle K Factor | Hood Number 1 | [11 empty] | No Filter
FILTER TYPE: | [13 empty] | 1 | No Filter | 0 | 0 | 0 | Filter Number | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | Captrate
Baffle K Factor | Filter #1 | Filter #2 | Filter #3 | Filter #4 | Filter #5 | Filter #6 | Filter #7 | Filter #8 | Filter #9 | Filter #10 | Filter #11 | Total CFM | CFM/ft | 2 | 10" x 16" | 0.78 | 1.34 | 1.28 | Combo Box Result | [11 empty] | Baffle | 1 | bar: 1 to 11
Filter Size | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter |  |  | 3 | 10" x 20" | 0.99 | 1.34 | 1.28 | Hood Number 2
Velocity | [13 empty] | 4 | 12" x 12" | 0.69 | 1.34 | 1.28 | Filter Number | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
CFM | [13 empty] | 5 | 12" x 16" | 0.97 | 1.34 | 1.28 | Combo Box Result | [12 empty] | 1 | bar: 1 to 11
[14 empty] | 6 | 12" x 20" | 1.25 | 1.34 | 1.28 | Hood Number 3
[14 empty] | 7 | 12" x 24" | 1.52 | 1.34 | 1.28 | Filter Number | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
Model = |  | Length = |  |  | Notes: | [8 empty] | 8 | 16" x 16" | 1.35 | 1.34 | 1.28 | Combo Box Result | [12 empty] | 1 | bar: 1 to 11
FILTER TYPE: | [13 empty] | 9 | 16" x 20" | 1.73 | 1.34 | 1.28 | Hood Number 4
Baffle K Factor | Filter #1 | Filter #2 | Filter #3 | Filter #4 | Filter #5 | Filter #6 | Filter #7 | Filter #8 | Filter #9 | Filter #10 | Filter #11 | Total CFM | CFM/ft | 10 | 16" x 25" | 2.22 | 1.34 | 1.28 | Filter Number | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
Filter Size | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter |  |  | 11 | 20" x 20" | 2.23 | 1.34 | 1.28 | Combo Box Result | [12 empty] | 1 | bar: 1 to 11
Velocity | [13 empty] | 12 | 20" x 25" | 2.85 | 1.34 | 1.28
CFM | [13 empty] | 13 | 24" x 24" | 3.36 | 1.34 | 1.28
Hood Number 3 Information | [13 empty] | *NOTE: You must use the longer standoffs when taking readings with the Evergreen Vel-Grid.
Model = |  | Length = |  |  | Notes:
FILTER TYPE:
Baffle K Factor | Filter #1 | Filter #2 | Filter #3 | Filter #4 | Filter #5 | Filter #6 | Filter #7 | Filter #8 | Filter #9 | Filter #10 | Filter #11 | Total CFM | CFM/ft
Filter Size | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter
Velocity
CFM
Hood Number 4 Information
Model = |  | Length = |  |  | Notes:
FILTER TYPE:
Baffle K Factor | Filter #1 | Filter #2 | Filter #3 | Filter #4 | Filter #5 | Filter #6 | Filter #7 | Filter #8 | Filter #9 | Filter #10 | Filter #11 | Total CFM | CFM/ft
Filter Size | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter
Velocity
CFM
Total Exhaust CFM's = |  | CFM

## PSP Supply
PSP Supply CFM Worksheet for Evergreen VelGrid
Job Number = | [16 empty] | rev. 2
Job Name =
PSP Number 1 Information | [18 empty] | PSP Information |  |  |  | PSP Reference Data
PSP Length = |  | inches | Notes: | [15 empty] | Reference | PSP Width | Free Area | K Factor | PSP Number 1
PSP Width = |  | inches | [16 empty] | 1 | 0 | 0 | 0 | Combo Box Result | 6
Number of Blanks = | [18 empty] | 2 | 6 | 0.5 | 0.88 | PSP Number 2
| Reading #1 | Reading #2 | Reading #3 | Reading #4 | Reading #5 | Reading #6 | Reading #7 | Reading #8 | Reading #9 | Reading #10 | Reading #11 | Reading #12 | Reading #13 | Reading #14 | Reading #15 | Reading #16 | CFM | CFM/ft | 3 | 9 | 0.75 | 0.88 | Combo Box Result | 6
Velocity | [18 empty] | 4 | 10 | 0.833 | 0.88 | PSP Number 3
[19 empty] | 5 | 12 | 1 | 0.88 | Combo Box Result | 6
PSP Number 2 Information | [18 empty] | 6 | 14 | 1.167 | 0.95 | PSP Number 4
PSP Length = |  | inches | Notes: | [15 empty] | 7 | 16 | 1.333 | 0.95 | Combo Box Result | 6
PSP Width = |  | inches | [16 empty] | 8 | 18 | 1.5 | 0.95
Number of Blanks = | [18 empty] | 9 | 20 | 1.667 | 0.95
| Reading #1 | Reading #2 | Reading #3 | Reading #4 | Reading #5 | Reading #6 | Reading #7 | Reading #8 | Reading #9 | Reading #10 | Reading #11 | Reading #12 | Reading #13 | Reading #14 | Reading #15 | Reading #16 | CFM | CFM/ft | 10 | 24 | 2 | 0.95
Velocity
*NOTE: You must use the longer standoffs when taking readings with the Evergreen Vel-Grid.
PSP Number 3 Information
PSP Length = |  | inches | Notes:
PSP Width = |  | inches
Number of Blanks =
| Reading #1 | Reading #2 | Reading #3 | Reading #4 | Reading #5 | Reading #6 | Reading #7 | Reading #8 | Reading #9 | Reading #10 | Reading #11 | Reading #12 | Reading #13 | Reading #14 | Reading #15 | Reading #16 | CFM | CFM/ft
Velocity
PSP Number 4 Information
PSP Length = |  | inches | Notes:
PSP Width = |  | inches
Number of Blanks =
| Reading #1 | Reading #2 | Reading #3 | Reading #4 | Reading #5 | Reading #6 | Reading #7 | Reading #8 | Reading #9 | Reading #10 | Reading #11 | Reading #12 | Reading #13 | Reading #14 | Reading #15 | Reading #16 | CFM | CFM/ft
Velocity
Total Supply CFM's = |  | CFM

## Supply Fan Filters
Supply Fan Filter CFM Worksheet for Evergreen VelGrid
Job Number = | [12 empty] | rev. 1
Job Name =
Supply Fan 1 Information | [13 empty] | Filter Information
Model = |  | Notes: | [11 empty] | Reference | Filter Size | Free Area | K Factor
| Filter #1 | Filter #2 | Filter #3 | Filter #4 | Filter #5 | Filter #6 | Filter #7 | Filter #8 | Filter #9 | Filter #10 | Filter #11 | Filter #12 | Total CFM | 1 | No Filter | 0 | 0
Filter Size | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter |  | 2 | 12" x 12" | 0.69 | 1.35
Velocity | [13 empty] | 3 | 12" x 16" | 0.97 | 1.35
CFM | [13 empty] | 4 | 12" x 20" | 1.25 | 1.35
[14 empty] | 5 | 12" x 24" | 1.52 | 1.35
Supply Fan 2 Information | [13 empty] | 6 | 16" x 16" | 1.36 | 1.35
Model = |  | Notes: | [11 empty] | 7 | 16" x 20" | 1.75 | 1.35
| Filter #1 | Filter #2 | Filter #3 | Filter #4 | Filter #5 | Filter #6 | Filter #7 | Filter #8 | Filter #9 | Filter #10 | Filter #11 | Filter #12 | Total CFM | 8 | 16" x 25" | 2.24 | 1.35
Filter Size | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter |  | 9 | 20" x 20" | 2.25 | 1.35
Velocity | [13 empty] | 10 | 20" x 25" | 2.88 | 1.35
CFM | [13 empty] | 11 | 24" x 24" | 3.36 | 1.35
Supply Fan 3 Information | [13 empty] | *NOTE: You must use the longer standoffs when taking readings with the Evergreen Vel-Grid.
Model = |  | Notes:
| Filter #1 | Filter #2 | Filter #3 | Filter #4 | Filter #5 | Filter #6 | Filter #7 | Filter #8 | Filter #9 | Filter #10 | Filter #11 | Filter #12 | Total CFM
Filter Size | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter
Velocity
CFM
Supply Fan 4 Information
Model = |  | Notes:
| Filter #1 | Filter #2 | Filter #3 | Filter #4 | Filter #5 | Filter #6 | Filter #7 | Filter #8 | Filter #9 | Filter #10 | Filter #11 | Filter #12 | Total CFM
Filter Size | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter
Velocity
CFM
Total Supply CFM's = |  | CFM

## HVC or Slot Filters
HVC or Slot Filter CFM Worksheet for Evergreen Airfoil
Job Number = | [6 empty] | 3 readings per filter | [6 empty] | rev. 0
Job Name =
Hood Number 1 Information | [14 empty] | Filter Information
Model = |  | Length = |  | Notes: | [10 empty] | Reference | Filter Size | Free Area | K Factor
| Filter #1 |  |  | Filter #2 | Filter #3 | Filter #4 | Filter #5 | Filter #6 | Filter #7 | Filter #8 | Filter #9 | Filter #10 | Filter #11 | Total CFM | 1 | No Filter | 0 | 0
Filter Size | No Filter |  |  | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter |  | 2 | 16" Wide | 0.2402 | 1
Velocity | [14 empty] | 3 | 20" Wide | 0.3027 | 1
CFM
Hood Number 2 Information | [15 empty] | Filter Opening = 2.25" x 19.375" or 15.375"
Model = |  | Length = |  | Notes:
| Filter #1 |  |  | Filter #2 | Filter #3 | Filter #4 | Filter #5 | Filter #6 | Filter #7 | Filter #8 | Filter #9 | Filter #10 | Filter #11 | Total CFM
Filter Size | No Filter |  |  | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter
Velocity
CFM
Hood Number 3 Information
Model = |  | Length = |  | Notes:
| Filter #1 |  |  | Filter #2 | Filter #3 | Filter #4 | Filter #5 | Filter #6 | Filter #7 | Filter #8 | Filter #9 | Filter #10 | Filter #11 | Total CFM
Filter Size | No Filter |  |  | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter
Velocity
CFM
Hood Number 4 Information
Model = |  | Length = |  | Notes:
| Filter #1 |  |  | Filter #2 | Filter #3 | Filter #4 | Filter #5 | Filter #6 | Filter #7 | Filter #8 | Filter #9 | Filter #10 | Filter #11 | Total CFM
Filter Size | No Filter |  |  | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter
Velocity
CFM
Total Exhaust CFM's = |  |  | CFM

## Condensate Baffle Filters
Condensate Baffle Filter CFM Worksheet for Evergreen Airfoil
Job Number = | [7 empty] | 3 Readings per Filter (Different Rows and Columns) | [6 empty] | rev. 0
Job Name =
Hood Number 1 Information | [15 empty] | Filter Information
Model = |  | Length = |  | Notes: | [11 empty] | Reference | Filter Size | Free Area | K Factor
| Filter #1 |  |  | Filter #2 | Filter #3 | Filter #4 | Filter #5 |  | Filter #6 | Filter #7 | Filter #8 | Filter #9 | Filter #10 | Filter #11 | Total CFM | 1 | No Filter | 0 | 0
Filter Size | No Filter |  |  | No Filter | No Filter | No Filter | No Filter |  | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter |  | 2 | 10" x 16" | 0.131 | 1
Velocity | [15 empty] | 3 | 10" x 20" | 0.196 | 1
CFM | [15 empty] | 4 | 12" x 16" | 0.131 | 1
[16 empty] | 5 | 12" x 20" | 0.196 | 1
Hood Number 2 Information | [15 empty] | 6 | 16" x 16" | 0.131 | 1
Model = |  | Length = |  | Notes: | [11 empty] | 7 | 16" x 20" | 0.196 | 1
| Filter #1 |  |  | Filter #2 | Filter #3 | Filter #4 | Filter #5 |  | Filter #6 | Filter #7 | Filter #8 | Filter #9 | Filter #10 | Filter #11 | Total CFM | 8 | 20" x 16" | 0.262 | 1
Filter Size | No Filter |  |  | No Filter | No Filter | No Filter | No Filter |  | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter |  | 9 | 20" x 20" | 0.349 | 1
Velocity
CFM
Hood Number 3 Information
Model = |  | Length = |  | Notes: | [12 empty] | Filter Opening = 2" Holes
| Filter #1 |  |  | Filter #2 | Filter #3 | Filter #4 | Filter #5 |  | Filter #6 | Filter #7 | Filter #8 | Filter #9 | Filter #10 | Filter #11 | Total CFM |  | 10" x 16" | 6 Holes
Filter Size | No Filter |  |  | No Filter | No Filter | No Filter | No Filter |  | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter |  |  | 10" x 20" | 9 Holes
Velocity | [16 empty] | 12" x 16" | 6 Holes
CFM | [16 empty] | 12" x 20" | 9 Holes
[17 empty] | 16" x 16" | 6 Holes
Hood Number 4 Information | [16 empty] | 16" x 20" | 9 Holes
Model = |  | Length = |  | Notes: | [12 empty] | 20" x 16" | 12 Holes
| Filter #1 |  |  | Filter #2 | Filter #3 | Filter #4 | Filter #5 |  | Filter #6 | Filter #7 | Filter #8 | Filter #9 | Filter #10 | Filter #11 | Total CFM |  | 20" x 20" | 16 Holes
Filter Size | No Filter |  |  | No Filter | No Filter | No Filter | No Filter |  | No Filter | No Filter | No Filter | No Filter | No Filter | No Filter
Velocity
CFM
Total Exhaust CFM's = |  |  | CFM

## Direct Fired Profile Pres. CFM
Direct Fired Heater Supply CFM For Given Burner Profile Pressure |  |  | Airflow Averages | [5 empty] | Slope |  |  |  |  | b |  |  |  |  | rev. 1
Job Number = |  |  | Profile Pressure | Size 1 | Size 2 | Size 3 | Size 4 | Size 5 | 1 | 2 | 3 | 4 | 5 | 1 | 2 | 3 | 4 | 5 |  | rev. 0
Heater Housing Size | Burner Profile Pressure* (In W.G.) | CFM** | 0
1 | 0 |  |  | 697.15 | 2035.5 | 1740.9 | 3037.188 | 4212.45
2 | 0 |  |  | 805.62 | 2400 | 1908.9 | 3537.504 | 9500
3 | 0 |  |  | 1166.76 | 2718.6 | 2289 | 3931.944 | 12730.5
4 | 0 |  |  | 1779.53 | 3000 | 4036.2 | 4444.716 | 15000
5 | 0 |  |  | 2036.25 | 3346.5 | 4676.7 | 4795.56 | 17008.5
|  |  |  | 2291.85 | 4000 | 4845 | 6439.752 | 19200
|  |  |  | 2450.196 | 5209.5 | 4979.1 | 6769.836 | 20976
*NOTE: Burner Profile Pressure is obtained with Evergreen by measuring the pressure drop between |  |  |  | 2655.768 | 5600 | 5159.7 | 6873.636 | 21800
the two Airflow probes located upstream and downstream of the burner assembly. |  |  |  | 2797.446 | 5778.75 | 6913.2 | 7500 | 22287
|  |  |  | 2958.57 | 6300 | 7919.1 | 13562.508 | 23500
**NOTE: CFM value obtained from predetermined formulas based off of a specified |  |  |  | 3139.14 | 6589.5 | 8820 | 16000 | 24598.5
burner profile pressure. |  |  | 100000

## Building Pressures
Building Pressures
Job Number = |  | rev. 0
Job Name =
Kitchen Pressure: | " W.C.
Dining Room Pressure: | " W.C.
Difference(Kitchen-Dining): | " W.C.